## Tables (hidden)
SheetName | TagType | Value | Address | Row | Column

## Configurations (hidden)
ApplyThresholds | TRUE
NumberFormat | FALSE
CellMerging | FALSE
DisplayOnlyMatchedMeasurements | FALSE
DisplayGraphPerMeasurement | TRUE
SheetName | AddMultipleSheets | Tables | PrimaryTable | PrimaryColumns | HasGroups | GroupTable | GroupColumns | NewSheetName
OTDR | TRUE | MatchedFilesDetails;Identification;OTDREventTable | MatchedFilesDetails | UniqueID | FALSE |  |  | OTDR
SheetName | Range | Filter
OTDR | $A$34:$M$35 | OTDREventTable.MeasurementType='OTDR'
Note on C7: mrupar1: Add semicolon separated table names which is used in sheet

## OTDR
Identification Information
Filename: | D P0305_007_1310.sor |  |  |  |  | Job ID:
Test date: | 19102023 |  |  |  |  | Customer:
Test time: | 16:12:38 (GMT+01:00) |  |  |  |  | Company: |  | Viavi
Comments:
Identifiers
Cable ID |  | Fiber ID |  |  | Location A |  |  | Location B |  |  | Kein
V04-06 |  | 31 |  |  | POP |  |  | 12344_Beispielstr_5
Location A | [5 empty] | Location B
Location: | POP |  |  |  |  | Location: |  | 12344_Beispielstr_5
Operator: | [5 empty] | Operator:
Unit model: | [5 empty] | Unit model:
Unit s/n: | 53645 |  |  |  |  | Unit s/n:
Calibration Date: | 1010001 |  |  |  |  | Calibration Date:
Test Parameters (1310 nm)
Range (km): |  | 40.6226 |  | Pulse (ns): |  |  | 30 |  | Duration (s): |  |  | 10
Results (1310 nm)
Span length (km): |  | 6.3195 |  | Span loss (dB): |  |  | 2.442 |  | Span ORL (dB): |  |  | 34.09
|  | Pass |  |  |  |  | Pass |  |  |  |  | Pass
Average loss (dB/km): |  | 0.386 |  | Avg. splice loss (dB): |  |  | 0.65 |  | Max. splice loss (dB): |  |  | 0.65
Graphic (1310 nm)
Event Table (1310 nm)
Type |  |  | No. | Location/ Length (km) |  | Loss (dB) |  | Reflectance (dB) |  | Attenuation (dB/km) |  | Cumulative (dB)
Launch Level |  |  |  | -1,0061 |  | 0,770 |  | -49.7
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 1.0061 |  | 0.324 |  |  |  | 0.322
Unknown
Non-Reflective |  |  | 1 | 0,0000 |  | 0,650 |  | --- |  |  |  | 0.65
[6 empty] | Pass |  | Unknown
Section |  |  |  | 6.3195 |  | 1.871 |  |  |  | 0.296 |  | 2.521
Unknown
Reflective |  |  | 2 | 6,3195 |  | -0,079 |  | -56.7 |  |  |  | 2.442
[6 empty] | Pass |  | Pass
Section |  |  |  | 1.0151 |  | 0.32 |  |  |  | 0.315
Unknown
Reflective |  |  |  | 7,3346 |  | 0,601 |  | -64.2
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 6.317 |  | 1.939 |  |  |  | 0.307
Unknown
Non-Reflective |  |  |  | 13,6515 |  | 0,000 |  | ---
[6 empty] | Unknown |  | Unknown
Markers Information (1310 nm) | [5 empty] | Manual Measurements (1310 nm)
Marker |  | Position (km) |  | Value (dB) |  | Measurement |  |  |  | Value
a |  | 1.3196 |  | 15.667 |  | 4 points event loss (dB) |  |  |  | -0.064
A |  | 6.3195 |  | 14.37 |  | A-B LSA loss (dB) |  |  |  | 1.487
B |  | 6.3304 |  | 14.332 |  | 2 points section att. (dB/km) |  |  |  | 3.501
b |  | 7.3346 |  | 13.898 |  | A-B LSA attenuation (dB/km) |  |  |  | 136.983
B-A |  | 0.0109 |  | 0.038 |  | 3 points reflectance (dB) |  |  |  | -76
[6 empty] | 3 points max. reflectance (dB) |  |  |  | -58.2
[6 empty] | A-B ORL (dB) |  |  |  | 54.87
Pass/Fail Thresholds (1310 nm)
Threshold |  | Fail |  | Warning
Splice loss (dB) |  | 1 |  | 1
Connector loss (dB) |  | 1 |  | 1
Splitter loss (dB) |  | --- |  | ---
Reflectance (dB) |  | -40 |  | -40
Fiber sect. att. (dB/km) |  | --- |  | ---
Span loss (dB) |  | 45 |  | 45
Span length (km) |  | 0 |  | 0
Span ORL (dB) |  | 15 |  | 15

## OTDR (2)
Identification Information
Filename: | D P0305_007_1550.sor |  |  |  |  | Job ID:
Test date: | 19102023 |  |  |  |  | Customer:
Test time: | 16:13:53 (GMT+01:00) |  |  |  |  | Company: |  | Viavi
Comments:
Identifiers
Cable ID |  | Fiber ID |  |  | Location A |  |  | Location B |  |  | Kein
V04-06 |  | 31 |  |  | POP |  |  | 12345_Beispielstr_5
Location A | [5 empty] | Location B
Location: | POP |  |  |  |  | Location: |  | 12345_Beispielstr_5
Operator: | [5 empty] | Operator:
Unit model: | [5 empty] | Unit model:
Unit s/n: | 53645 |  |  |  |  | Unit s/n:
Calibration Date: | 1010001 |  |  |  |  | Calibration Date:
Test Parameters (1550 nm)
Range (km): |  | 40.6394 |  | Pulse (ns): |  |  | 100 |  | Duration (s): |  |  | 10
Results (1550 nm)
Span length (km): |  | 6.3103 |  | Span loss (dB): |  |  | 1.606 |  | Span ORL (dB): |  |  | 35.48
|  | Pass |  |  |  |  | Pass |  |  |  |  | Pass
Average loss (dB/km): |  | 0.254 |  | Avg. splice loss (dB): |  |  | -0.078 |  | Max. splice loss (dB): |  |  | -0.078
Graphic (1550 nm)
Event Table (1550 nm)
Type |  |  | No. | Location/ Length (km) |  | Loss (dB) |  | Reflectance (dB) |  | Attenuation (dB/km) |  | Cumulative (dB)
Launch Level |  |  |  | -1,0134 |  | 0,595 |  | -52.5
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 1.0134 |  | 0.169 |  |  |  | 0.167
Unknown
Reflective |  |  | 1 | 0,0000 |  | 0,551 |  | -72.3 |  |  |  | 0.551
[6 empty] | Pass |  | Pass
Section |  |  |  | 5.422 |  | 0.992 |  |  |  | 0.183 |  | 1.543
Unknown
Non-Reflective |  |  | 2 | 5,4220 |  | -0,078 |  | --- |  |  |  | 1.465
[6 empty] | Pass |  | Unknown
Section |  |  |  | 0.8883 |  | 0.155 |  |  |  | 0.175 |  | 1.62
Unknown
Reflective |  |  | 3 | 6,3103 |  | -0,015 |  | -57.8 |  |  |  | 1.605
[6 empty] | Pass |  | Pass
Section |  |  |  | 1.0236 |  | 0.184 |  |  |  | 0.18
Unknown
Non-Reflective |  |  |  | 7,3340 |  | 0,582 |  | ---
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 0.8807 |  | 0.144 |  |  |  | 0.164
Unknown
Non-Reflective |  |  |  | 8,2147 |  | -0,060 |  | ---
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 5.4271 |  | 0.988 |  |  |  | 0.182
Unknown
Reflective |  |  |  | 13,6418 |  | 0,000 |  | -57.2
[6 empty] | Unknown |  | Unknown
Markers Information (1550 nm) | [5 empty] | Manual Measurements (1550 nm)
Marker |  | Position (km) |  | Value (dB) |  | Measurement |  |  |  | Value
a |  | 5.4628 |  | 24.609 |  | 4 points event loss (dB) |  |  |  | -0.015
A |  | 6.3103 |  | 24.428 |  | A-B LSA loss (dB) |  |  |  | 1.015
B |  | 6.341 |  | 24.456 |  | 2 points section att. (dB/km) |  |  |  | -0.914
b |  | 7.334 |  | 24.302 |  | A-B LSA attenuation (dB/km) |  |  |  | 33.13
B-A |  | 0.0306 |  | -0.028 |  | 3 points reflectance (dB) |  |  |  | -80.5
[6 empty] | 3 points max. reflectance (dB) |  |  |  | -57.8
[6 empty] | A-B ORL (dB) |  |  |  | 53.7
Pass/Fail Thresholds (1550 nm)
Threshold |  | Fail |  | Warning
Splice loss (dB) |  | 1 |  | 1
Connector loss (dB) |  | 1 |  | 1
Splitter loss (dB) |  | --- |  | ---
Reflectance (dB) |  | -40 |  | -40
Fiber sect. att. (dB/km) |  | --- |  | ---
Span loss (dB) |  | 45 |  | 45
Span length (km) |  | 0 |  | 0
Span ORL (dB) |  | 15 |  | 15

## OTDR (3)
Identification Information
Filename: | D P0305_007_1625.sor |  |  |  |  | Job ID:
Test date: | 19102023 |  |  |  |  | Customer:
Test time: | 16:14:43 (GMT+01:00) |  |  |  |  | Company: |  | Viavi
Comments:
Identifiers
Cable ID |  | Fiber ID |  |  | Location A |  |  | Location B |  |  | Kein
V04-06 |  | 31 |  |  | POP |  |  | 12345_Beispielstr_5
Location A | [5 empty] | Location B
Location: | POP |  |  |  |  | Location: |  | 12345_Beispielstr_5
Operator: | [5 empty] | Operator:
Unit model: | [5 empty] | Unit model:
Unit s/n: | 53645 |  |  |  |  | Unit s/n:
Calibration Date: | 1010001 |  |  |  |  | Calibration Date:
Test Parameters (1625 nm)
Range (km): |  | 40.595 |  | Pulse (ns): |  |  | 30 |  | Duration (s): |  |  | 10
Results (1625 nm)
Span length (km): |  | 6.3159 |  | Span loss (dB): |  |  | 1.753 |  | Span ORL (dB): |  |  | 35.2
|  | Pass |  |  |  |  | Pass |  |  |  |  | Pass
Average loss (dB/km): |  | 0.278 |  | Avg. splice loss (dB): |  |  | -0.075 |  | Max. splice loss (dB): |  |  | -0.075
Graphic (1625 nm)
Event Table (1625 nm)
Type |  |  | No. | Location/ Length (km) |  | Loss (dB) |  | Reflectance (dB) |  | Attenuation (dB/km) |  | Cumulative (dB)
Launch Level |  |  |  | -1,0099 |  | 0,000 |  | -54
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 1.0099 |  | 0.201 |  |  |  | 0.199
Unknown
Reflective |  |  | 1 | 0,0000 |  | 0,538 |  | -67.6 |  |  |  | 0.538
[6 empty] | Pass |  | Pass
Section |  |  |  | 5.4335 |  | 1.054 |  |  |  | 0.194 |  | 1.592
Unknown
Non-Reflective |  |  | 2 | 5,4335 |  | -0,075 |  | --- |  |  |  | 1.517
[6 empty] | Pass |  | Unknown
Section |  |  |  | 0.8823 |  | 0.183 |  |  |  | 0.207 |  | 1.7
Unknown
Reflective |  |  | 3 | 6,3159 |  | 0,053 |  | -57.5 |  |  |  | 1.753
[6 empty] | Pass |  | Pass
Section |  |  |  | 1.0112 |  | 0.194 |  |  |  | 0.192
Unknown
Non-Reflective |  |  |  | 7,3270 |  | 0,548 |  | ---
[6 empty] | Unknown |  | Unknown
Section |  |  |  | 6.3197 |  | 1.169 |  |  |  | 0.185
Unknown
Reflective |  |  |  | 13,6467 |  | 0,000 |  | -55.4
[6 empty] | Unknown |  | Unknown
Markers Information (1625 nm) | [5 empty] | Manual Measurements (1625 nm)
Marker |  | Position (km) |  | Value (dB) |  | Measurement |  |  |  | Value
a |  | -0.9895 |  | 19.537 |  | 4 points event loss (dB) |  |  |  | 0.539
A |  | 0 |  | 19.281 |  | A-B LSA loss (dB) |  |  |  | 1.154
B |  | 0.0115 |  | 18.798 |  | 2 points section att. (dB/km) |  |  |  | 42.061
b |  | 5.0112 |  | 17.822 |  | A-B LSA attenuation (dB/km) |  |  |  | 100.517
B-A |  | 0.0115 |  | 0.483 |  | 3 points reflectance (dB) |  |  |  | *****
[6 empty] | 3 points max. reflectance (dB) |  |  |  | -69
[6 empty] | A-B ORL (dB) |  |  |  | 59.94
Pass/Fail Thresholds (1625 nm)
Threshold |  | Fail |  | Warning
Splice loss (dB) |  | 1 |  | 1
Connector loss (dB) |  | 1 |  | 1
Splitter loss (dB) |  | --- |  | ---
Reflectance (dB) |  | -40 |  | -40
Fiber sect. att. (dB/km) |  | --- |  | ---
Span loss (dB) |  | 45 |  | 45
Span length (km) |  | 0 |  | 0
Span ORL (dB) |  | 15 |  | 15